## BOQ
Item | Description of Work | Unit | Qty. | Rate | Amount
|  |  |  | US$ C | US$ | C
1 | BILL-1- Preliminary and General
1.1 | Preliminary | Item | Item
(includes Site Establishment/ Office, Transportation, Equipment, Test, storage etc required by the Contractor)
1.2 | Allow for attendance at any and all inspections, testing and meetings required by the Consulting Engineers | Item | Item
1.3 | Allow for attendance at any and all site meetings required by the Engineer | Item | Item
1.4 | Allow for protection of Fire Alarm Installation upto Testing and Commissioning stage | Item | Item
1.5 | Provide Compliance Certificate at all stages of the installation (e.g. First Fix, Second Fix & Final Fix) | Item | Item
1.6 | Provide Two Sets of "As Built" drawings of the Electrical Installation | Item | Item
1.7 | Allow for any other item not provided for in the Schedule of Quantities | Item | Item
(Detailed as below)
Note the client will provide mobile high lift stairs for use by the contractor, but the contractor must allow for mobile scaffolding for use on site
Where not stated in the BOQ the Techical Specifications and Drawinsg will take precedence over the BOQ. The contractor must take note of this when pricing
This is an operational site and as such the contractor must be aware that work schedules will be dictated by the client and as such the contractor must allow for out of hours and non-sequencec works in order to avoid any inconvenience to the client.
Note: Above mentioned items need to be priced item wise, and no Lump Sum to be stated.
| Sub-Total of Bill 1- Preliminary and General Carried to Main Summary |  |  | US$
BILL -02: ELECTRICAL WORKS
2.1 | DISTRIBUTION BOARDS
Supply, deliver, erect, install, connect and set to work the following Distribution Boards and all accessories as specified and indicated on all relevant drawings c/w labelling & blank covers. (Refer drg. No. DH27/2020/E02
All MCCB's ; MCB's to be CBI Hymag or Merlin Gerin Make or Legrand with required Short Circuit rating
2.1.1 | DB-FP ( Distribution Board - Fire Pump)
6 way TPN, Surface mounted, Orange in colour, Lockable, Weatherproof Type consisting of followings:
250A TP+N Cu. Bus-bars
01 No. 250A TP MCCB, 25kA Incomer
01 No. 250A TP Contractor
01 No.200A TP MCCB, 15kA
01 No. 10A TP MCB, 10kA
03 No.TP Spare Ways c/w blank covers
01 No. 250A TP Contractor connected to the Fire Sprinkler system
| 1 No. Earth Bar | Item | 1
2.1.2 | 01 No. 250A TP MCCB, 25kA in existing MDB | No. | 1
2.1.3 | DB-I ( Distribution Board - Inverter)
6 way SPN, Surface mounted, White in colour, Lockable, DB consisting of followings:
01 No. 30A SP MCB, 10kA, Incomer
02 No. 20A SP MCB, 10kA
1 No. Earth Bar
| 1 No. Neutral Bar | Item | 1
2.2 | CABLES C/w ACCESSORIES
(Refer drg. No. DH27/2020/E02)
Supply, deliver, erect, install, connect and set to work the following Cables including cable glands, lugs, supports and accessories:
2.2.1 | Existing Main Distribution Board- (MDB) Essential Power to DB-FP in 4CORE 95 mm sq. PVC/SWA/PVC Cable + 35mm sq BCEC | M | 150
2.2.2 | DB-FP to FIRE PUMP in 4Core 70 mm Sq. PVC/SWA/PVC Cable + 25 mm Sq. BCEC | M | 25
2.2.3 | DB-FP to JOCKEY PUMP in 4Core 2.5 mm Sq. PVC/SWA/PVC Cable + 1.5 mm Sq. BCEC | M | 25
2.2.4 | Existing DB to DB-I in 3Core 6.0 mm Sq. PVC/SWA/PVC Cable | M | 25
2.3 | SOCKET OUTLETS c/w WIRING
2.3.1 | 13Amp Single Switch Socket outlet in 3 core 2.5 mm sq PVC/Cu. Flexible cable (10 Meters) in PVC Conduit from the DB-I/ P1 | No. | 1
2.3.2 | 13Amp Single Switch Socket outlet in 3 core 2.5 mm sq PVC/Cu. Flexible cable (100 Meters) in PVC Conduit from the DB-I/P1 | No. | 1
2.4 | CABLE TRAYS & WIRING DUCTS C/W ACCESSORIES
Supply, deliver, install the following Cable Trays/Wiring duct (P2000), Bends, Tee, c/w mounting Brackets (Mounting brackets spacing should not be not less than 1.2 meter) and all required accessories.
(Refer drg. No. DH27/2020/E01, 02 )
CABLE TRAYS
2.4.1 | 152x38mm Hieght, Medium Duty Perforated Cable Tray c/w Mounting Bracket at each.1.5 Meter for Telephone/Data Cable- Make "Cabstrut or Eqv." | M | 150
2.4.2 | 152x38mm Medium Duty External/Internal Elbow (Bend) - Make "Cabstrut or Eqv." | No. | 4
WIRING DUCT
2.4.3 | 41mmx41mm GI Wiring Duct c/w all required accessories for Electrical Cable- Make "Cabstrut-P2000/1.5mm." | M | 20
| Sub-Total of Bill 2- Electrical Works, Carried to Main Summary |  |  | US$
3 | INVERTER
Supply, deliver, erect, install, connect and set to work the following Inverter c/w Batteries and all required accessories
3.1 | 2.5kVA 48V DC Inverter | No. | 1
3.2 | 200AH 12V SOLAR BATTERIES | No. | 4
| Sub-Total of Bill 3- Inverter c/w batteries, Carried to main Summary |  |  | US$
4 | FIRE ALARM RETICULATION
(Refer drg. No. DH27/2020/E01, 02 )
Supply, deliver, install & set to work the following Fire Alarm Panel and accessories including cabling in "Fire Retardent Cables"
4.1 | Intelligent Addressable Fire Alarm Panel -2 Loop c/w Network Card and 72 hour Battery back-up, Make -EATON CF1200NC | No. | 2
4.2 | Fire Alarm Sounder, Make EATON COPWS | No. | 23
4.3 | Fire Alarm Sounder -Weatherproof Type, Make EATON COPWS-WP | No. | 7
4.4 | Loop Connected LED Becon -Weatherproof Type, Make EATON | No. | 1
4.5 | Intelligent Addressable Manual Fire Alarm Break Glass Unit, Make EATON COPBGU-S | No. | 25
4.6 | Optical Smoke Detector, Make EATON COPP420 | No. | 320
4.7 | Fire Retardant cable- 2.5mm sq PVC/Cu in 25mm sq PVC Conduit to connect Fire Panels to Break Glass, Sounder, Smoke Detectors | M | 3600
4.8 | Installation / Labour Charges, Test and Commissioning | Item | Item
| Sub-Total of Bill 3, Fire Alarm Installation Carried to Main Summary |  |  | US$
MAIN SUMMARY- FIRE ALARM INSTALLATION WORKS
Bill No. | Description of Work |  |  |  | Amount
[5 empty] | US$ | C
1 | Preliminary and General
2 | Electrical Works
3 | Inverter
4 | Fire Alarm Installation
5 | Allow Contingency
Note: 1) The Main Power supply Cable to DB-FP has been estimated at 150 Meters. However as per Site measurement, the Quantity may vary.
2) No Major Builder's works has been measured
| SUB TOTAL |  |  | US$
| VAT (16%) |  |  | US$
| TOTAL AMOUNT |  |  | US$
Total Amount in words: US Dollar……………………………………………………………………….
…….…..………………………………………………………………………………………………
Contractor's Name and Address:
| Date:……………………… |  |  | Signed:………………………….

## COVER
BILL OF QUANTITIES
FOR
FIRE ALARM RETICULATION INSTALLATION AT WAREHOUSES FOR MEDICAL STORES LTD HEAD OFFICES ON MUKWA ROAD, LUSAKA
FOR
MEDICAL STORES LTD
CONSULTING ENGINEERS AND PROJECT MANAGER : CLIENT CLIENT:
DH ENGINEERING CONSULTANTS LTD MEDICAL STORES LTD
P.O. BOX: 37928 P O BOX : 30207
LUSAKA LUSAKA,
ZAMBIA ZAMBIA