## BILL N0.1 P&Gs
FIRE SPRINKLER
SYSTEM
ITEM | DESCRIPTION | UNIT | QTY | RATE | USD
PROPOSED FIRE SPRINKLER SYSTEM AT
MEDICAL STORES LIMITED
BILL NO. 1
PRELIMINARY AND GENERAL ITEMS
A | The Tenderer is to allow for all Contract Preliminaries which
he considers necessary to comply with all his obligations
and all his charges including access to site, general
attendance, security of works, all materials, tools and
equipment, supervision and labour, possession
and completion of works, variations, possession, fluctuations
| terms of paymenT, antiquities and arbitration |  | Item
B | Testing , Commissioning and training of the end user . |  | Item
C | Operation and Maintenance Manuals |  | Item
D | Client will provide use of in house High Lift Stairs for use
by the contractor. Water and Power will also be provided at
no cost by the Client.
Contractor must allow for installation of their own scaffolding
where required. Preferably mobile scaffolding as the premises
will be operation during installation
E | Contractor must allow for the fact that the site is an operational
facility and allowance must be made to work to the client's
schedule and out of hours where required to avoid any
inconvenience to the client's operations
F | Technical Specifications and Drawings have been provided for
the Fire Sprinkler System.
The Technical Specifications and Drawings will take precedence
over the Bills of Quantities where a discerepancy arises.
When pricing reference to these two documents must be made
G | Allow for 12 months warranty on all equipment and
workmanship as well as call out service to attend to any defects
During this period servicjng and tresting of fire sprinkler
| equipment is to be provided |  | item
H | Allow for Bonds and Insurances as required |  | item
I | Allow for the provision of all PPE, compliance to Covid-19 regulations, preparation and submission of a Health and Safety Plan and compliance to the Cliwent's Health and safety Regulations on site |  | item
J | The Tenderer is advised that should he require to insert
prices for any items not specifically included above which he
considers necessary in order to comply with all his
obligations under the Contract Documents, he shall list
them below and insert the prices in the Money Column
| TOTAL CARRIED TO GENERAL SUMMARY |  |  | USD | 0

## BILL NO.2 NEW WAREHOUSE
| SUPPLY, INSTALL AND SET TO WORK |  |  |  | FIRE SPRINKLER
SYSTEM
ITEM | DESCRIPTION | UNIT | QTY | RATE | USD
BILL NO.2
NEW WAREHOUSE
SOLID DRAWN MEDIUM DUTY MILD STEEL SCHED 40
PIPING AND FIXING in accordance with the
recommended manufacturer's instructions and as shown
on relevant drawings
A | 25mm Diameter peuc pipe fixed to and including hangers fixed to steel roof structure. Include for painting of all pipwork with primer, undercoat and final coat of signal red. | m | 350
B | 100mm Ditto | m | 120
C | 80mm Ditto | m | 320
D | 65mm Ditto | m | 960
E | 50mm Ditto | m | 980
F | 150mm Ditto | m | 135
G | 200mm Ditto | m | 125
Extra over the foregoing pipework for the following
fittings
H | 100mm Grooved coupling | no | 20
J | 80mm Grooved coupling | no | 30
K | 65mm Grooved coupling | no | 90
L | 50mm Socket | no | 180
M | 25mm Socket | no | 340
N | 25x15mm Reducing socket | no | 450
O | 100mm W/on flange | no | 25
P | 150mm Grooved Coupling | no | 25
Q | 200mm Grooved Coupling | no | 20
| Carried to Collection |  |  | USD
FIRE SPRINKLER
SYSTEM
ITEM | DESCRIPTION | UNIT | QTY | RATE | USD
A | 100mm W/on elbow | no | 11
C | 25mm F/F Elbow | no | 20
D | 100mm Belts | no | 51
E | 80mm Belts | no | 119
F | 65mm Belt | no | 343
G | 50mm Belt | no | 373
K | 25mm Belt | no | 106
L | 150mm Belts | no | 55
M | 200mm Belts | no | 52
N | M12 Drop ion anchor | no | 911
O | M8 Drop in anchor | no | 462
P | 12mm Threaded rod | m | 500
Q | 8mm Threaded rod | m | 417
R | 12mm Nut | no | 198
S | 8mm Nut | no | 137
FIRE SPRINKLER HEADS
T | 15mm Brass pendant 68 degrees conventional automatic
sprinkler head with white ceiling rosette as described with
| operating temperature of 68 / 78 degrees celsius and jointing | No | 340
complete with heat shield on each sprinkler head
PAINTING
U | Apply one coat etching primer and paint two coats red gloss
| enamel to all pipes | m | 485
V | Ditto to large pipes | m | 1692
SIREN AND STROBE LIGHT
W | Include for Siren and Strobe Light linked to Fire Pump to activate when Fire Pump Runs | No | 2
DRAIN TEST VALVE
X | Supply and set to work the drain test point valve complete with all necessary accessories, pressure gauges as required by the engineer. | No | 1
| Carried to Collection |  |  | USD

## BILL NO. 3 EXISTING WAREHOUSE
| SUPPLY, INSTALL AND SET TO WORK |  |  |  | FIRE SPRINKLER
SYSTEM
ITEM | DESCRIPTION | UNIT | QTY | RATE | USD
BILL NO.3
EXISTING WARE HOUSE
EXISTING PIPEWORK
A | Remove existing fire sprinkler pipework and sprinkler heads and hand back to Client. Disconnect existing Fire water Supply and Plug Off | Item
SOLID DRAWN MEDIUM DUTY MILD STEEL SCHED 40
PIPING AND FIXING in accordance with the
recommended manufacturer's instructions and as shown
on relevant drawings
A | 25mm Diameter peuc pipe fixed to and including hangers fixed to to steel roof structure. Include for painting of all pipwork with primer, undercoat and final coat of signal red. | m | 620
B | 100mm Ditto | m | 410
C | 80mm Ditto | m | 230
D | 65mm Ditto | m | 860
E | 50mm Ditto | m | 680
F | 150mm Ditto | m | 220
G | 200mm Ditto | m | 96
Extra over the foregoing pipework for the following
fittings
H | 100mm Grooved coupling | no | 40
J | 80mm Grooved coupling | no | 36
K | 65mm Grooved coupling | no | 150
L | 50mm Socket | no | 120
M | 25mm Socket | no | 410
N | 25x15mm Reducing socket | no | 400
O | 100mm W/on flange | no | 36
P | 150mm Grooved Coupling | no | 30
Q | 200mm Grooved Coupling | no | 34
| Carried to Collection |  |  | USD
FIRE SPRINKLER
SYSTEM
ITEM | DESCRIPTION | UNIT | QTY | RATE | USD
A | 100mm W/on elbow | no | 12
C | 25mm F/F Elbow | no | 19
D | 100mm Belts | no | 165
E | 80mm Belts | no | 92
F | 65mm Belt | no | 416
G | 50mm Belt | no | 336
K | 25mm Belt | no | 105
L | 150mm Belts | no | 107
M | 200mm Belts | no | 41
N | M12 Drop ion anchor | no | 1254
O | M8 Drop in anchor | no | 562
P | 12mm Threaded rod | m | 789
Q | 8mm Threaded rod | m | 504
R | 12mm Nut | no | 260
S | 8mm Nut | no | 125
FIRE SPRINKLER HEADS
T | 15mm Brass pendant 68 degrees conventional automatic
sprinkler head with white ceiling rosette as described with
| operating temperature of 68 / 78 degrees celcius and jointing | No | 368
complete with heat shield on each sprinkler head
PAINTING
U | Apply one coat etching primer and paint two coats red gloss
| enamel to all pipes | m | 1404
V | Ditto to large pipes | m | 1036
SIREN AND STROBE LIGHT
W | Include for Siren and Strobe Light linked to Fire Pump to activate when Fire Pump Runs | No | 2
DRAIN TEST VALVE
X | Supply and set to work the drain test point valve complete with all necessary accessories, Pressure guages and BMS connection as required by the engineer. | No | 1
| Carried to Collection |  |  | USD

## BILL N0.4 MAINS CONNECTION
| SUPPLY, INSTALL AND SET TO WORK |  |  |  | FIRE SPRINKLER
SYSTEM
ITEM | DESCRIPTION | UNIT | QTY | RATE | USD
BILL NO.4
CONNECTING MAINS
SEAMLESS SCH.40 Mild Steel Pipes
all in accordance with the manufacturer's instructions
A | Above Ground mounted 300mm seamless Sch. 40 carbon steel Pipes with steel pipe supports and concrete plinths fixed to ground. Include for painting of all pipework with primer, undercoat and final coat of signal red. | m | 12
B | 200mm Diameter peuc pipe fixed to and including hangers fixed to walls, or to steel roof structure. Include for painting of all pipwork with primer, undercoat and final coat of signal red. | m | 95
Extra over the foregoing pipework for the following
fittings
C | 300mm Grooved coupling | no | 12
D | 200mm Grooved coupling | no | 26
E | 300x200mm W/on reducer | no | 2
F | 200mm W/on tee | no | 2
Extra over the foregoing pipework for the following
fittings (cont'd)
G | 200mm Socket union | no | 26
H | 150mm Equal tee | no | 22
I | 50mm Socket | no | 30
J | 50x50x5mm Angle iron | no | 26
K | 300mm VJ coupling | no | 6
L | M16 Threaded rod | m | 42
M | M12 Threaded rod | m | 24
N | M16 Nut | no | 66
P | M12 Nut | no | 44
Q | Insertion rubber | m | 12
R | Anti vibration on the suction line and the test line | no | 4
S | Vortex inhibitors | no | 2
Istallation Control Valves (ICV)
T | Supply and fit and set to work installation control valves complete with all necessary fittings as detailed on drawings and specifications | no | 2
| Carried to Collection |  |  | USD
Note on F59: Ashley:

## BILL N0.5 TANK AND FIRE PUMP
| SUPPLY, INSTALL AND SET TO WORK |  |  |  | FIRE SPRINKLER
SYSTEM
ITEM | DESCRIPTION | UNIT | QTY | RATE | USD
BILL NO.5
WATER TANK AND FIRE PUMPS
FIRE PUMPS
A | ASIB Approved Containerised Centrifugal Fire Pumpset as Davron
comprising 2 X duty and 1 X jockey pumps as described
as described or equivalent fully approved manufacturer with
Minimum Capacity:2900 l /m @80 m HD
1 | 75.0 KW, 3PHASE /50Hz/ 380V (Electric pump) complete installed
Comprising:
- Pressure switches
- Red warning light for fixing on valve chamber
- Control panels as described
- Anti-vibration mounts
2 | 66 KW,3 PHASE (Diesel )
Comprising:
- Pressure switches
- Red warning light for fixing on valve chamber
- Control panels as described
- Anti-vibration mounts
3 | Pressure maintaining 1.1 KW "Jockey" pump as described all by a fully
approved manufacturer and suitable for automatic operation by
water pressure switch with:
Capacity: 20litres / minute at 5.5 bars
Power Source: 380V/3Phase/50Hz
Comprising:
- Pressure switch
- Control panel as described
| - Anti-vibration mounts | Set | 1
Complete with external siren and strobe light to indicate Fire Pump is running
STEEL TANK
B | 215,000 litres Capacity "ABECO", or approved equivalent, Steel Paneled water Tank to be mounted on concrete plinth to engineers approval. Complete with all valves and pipework related,drain pipes,spare blanked off openings , inlet and suction lines including pump test line as per drawing. Tank to be vertically partitioned 50/50 to allow for maintenance and ensure continuity of operation. | no | 1
PUMP CONTAINER AND TANK CIVIL WORKS CONSTRUCTION
C | Allow for the construction of the containerised pump supports as per manufacturer's details | lot
D | Allow for the construction of the tank concrete plinths according to engineer's design and details.The contractor to include for 3 concrete tests from each batch of concrete cast. | lot
PUMP HOUSE ELECTRICITY SUPPLY
E | Allow for electricity supply to the pump set from pump DB to be tested and certified by electrical engineer. | lot
TESTING OF FIRE FIGHTING SYSTEM
F | Include for carrying out in the presence of the Engineer a static
pressure test at the furthest point on each system to 1.5 times
| the maximum operating pressure i.e. 16 bar |  | Item
G | Include for carrying out in the presence of the Engineer a
discharge test on any sprinkler outlet to be decided by the
| Engineer. The Contractor or his Subcontractor shall provide a hose |  | Item
connection and length of 25mm hose to lead the discharge to
outside the building
j | Include for carrying out in the presence of the Engineer a
| running pressure test as required by L.P.C Rules |  | Item
k | Include for carrying out in the presence of the Engineer a test
of the hydraulic alarm system
l | Allow for hydraulic caculations to be provided by the contractor prior to procurement of equipment and submitted to the Engineer for approval . |  | item
| Carried to Collection |  |  | USD

## SUMMARY
FIRE SPRINKLER
SYSTEM
SUMMARY
ITEM | DESCRIPTION | UNIT | QTY | USD
PROPOSED FIRE SPRINKLER SYSTEM FOR THE PROPOSED LABORATORIES AND OFFICE BUILDING FOR ZAMRA
GENERAL SUMMARY
1 | BILL NO.1 PRELIMINARY AND GENERAL ITEMS
2 | BILL NO.2 NEW WAREHOUSE
3 | BILL NO.3 EXISTING WAREHOUSE
4 | BILL NO.4 MAINS CONNECTION
5 | BILL NO.5 TANK AND FIRE PUMP
6 | SPARES AS DESCRIBED IN THE TECHNICAL SPECIFICATION
7 | ALLOW A CONTINGENCY 5%
USD
| ADD VAT @ 16% |  | USD
| TOTAL AMOUNT OF OFFER |  | USD
NO FLUCTUATIONS CLAUSE
There will be no fluctuations on this contract.The Contract
rates are FIXED in US Dollars and payment for work done
will be made in same currency.
Name Contractor:…………………………………..
Signature:…………………………………………..
Date:………………………………………………….
VALIDITY OF QUOTATION